APS Large Load Interconnection Process

Arizona Public Service — Data Center / Extra-Large Load Reference

Prepared for Site Selection  ·  Fluidstack  ·  June 2026

Confidence basis: Rate terms are GROUNDED in the current APS XHLF tariff (A.C.C. No. 6067, Rev 3, eff. March 8, 2024, Decision No. 79293). Process stage map and timelines are ESTIMATED — no APS large-load process guide or facilities study is on file. Collateral and minimum-bill amounts are set per Electric Supply Agreement and are not publicly fixed. Verify against live ACC dockets before any commitment.

# 1.  Market Context

Arizona is NOT an organized ISO/RTO market. There is no independent interconnection queue, no LMP energy market, and no FERC ISO tariff governing load interconnection. APS is vertically integrated and is its own Balancing Authority within WECC — it owns both the wires and the generation. Practical implications:

you negotiate directly with one entity, and “can they serve it” is a generation-adequacy question, not just a wires question.

the process is governed by state-filed tariffs and line-extension schedules, regulated by the Arizona Corporation Commission (ACC) — not FERC ISO rules.

the ACC can change rates and tariff terms mid-project — a live regulatory risk unique to this structure.

Arizona is capacity- and transmission-constrained in high-growth corridors (Phoenix metro, Buckeye, Coolidge, Casa Grande). APS large-customer peak demand ≈ 13.1 GW (2026); pending data-center interest reported at ~10–18 GW.

“bring your own power” (customer-assigned new generation) is an explicit policy direction, not a fringe option.

# 2.  Process Map

Position a project against these stages. The firm gate is Stage 6 — nothing before it is a committed power position.

| # | Stage | Typical Duration | Owner |
| --- | --- | --- | --- |
| 1 | Load request to APS large-load / new-service team (MW, location, ramp, in-service date) | Customer action | Customer |
| 2 | Preliminary capacity / feasibility screening (can APS serve it at that location/size/timing) | 1–3 months [EST] | APS |
| 3 | Study agreement + deposit → detailed facilities / system-impact study | 3–6 months [EST] | APS |
| 4 | Commercial commitments: ESA negotiation, site control, collateral, ramp + minimum-bill terms | Costs begin accruing | Customer / APS |
| 5 | ESA + Line Extension Agreement (Service Schedule 3) executed; ACC approval if special contract | 2–6 months [EST] | APS / ACC |
| 6 | CIAC paid + collateral posted → APS orders long-lead equipment ★ FIRM GATE | Customer action | Customer |
| 7 | Engineering + construction (substation / transmission) | 24–48+ months [EST] | APS |
| 8 | Energization | — | APS |

Total duration: ~36–60 months [ESTIMATED] — gated by transformer lead times and area capacity, not engineering. Clock starts at the study agreement (Stage 3); hard cost accrual begins at Stage 4.

# 3.  Path to Firm Power

Firm gate = executed ESA + executed Line Extension Agreement (Service Schedule 3),

plus CIAC paid / collateral posted,

plus ACC approval if the deal is a special contract — which together trigger equipment procurement.

Anything earlier — a feasibility study, a draft ESA — is non-firm and not something APS will build against. The cheap optionality sits in the study stage; real capital exposure is the CIAC + collateral at the firm gate.

# 4.  Cost & Rate Terms (XHLF Tariff)

Grounded in APS Rate Schedule XHLF (A.C.C. No. 6067, Rev 3). XHLF is the large-load rate vehicle for extra-high-load-factor customers such as data centers.

### Eligibility

| Requirement | Threshold | Source |
| --- | --- | --- |
| Monthly maximum demand | ≥ 5,000 kW | GROUNDED |
| Load factor | ≥ 92% for ≥ 9 of prior 12 months | GROUNDED |
| Econ-Dev & Sustainability features | ≥ 15,000 kW + 50% carbon-free activity | GROUNDED |

### Charges

| Charge | Transmission | Primary | Secondary |
| --- | --- | --- | --- |
| Energy ($/kWh) | 0.04210 | 0.04210 | 0.04210 |
| Demand ($/kW) | 13.274 | 17.290 | 18.750 |
| Basic service ($/day) | 43.130 | 8.833 | 5.682 |

Econ-Dev discount: up to 35% off the Generation–Capacity charge, ≤ 6 years, new load only (Service Schedule 9).

Optional market-proxy energy: ICE Palo Verde hub day-ahead on/off-peak + $0.00314/kWh non-bypassable fee (in lieu of standard fuel adjustment).

Program cap: Econ-Dev/Sustainability program limited to +50 MW/yr per customer, 500 MW total (APS discretion on market liquidity).

# 5.  Interconnection Process Costs

Read this first: APS does NOT publish a flat large-LOAD study fee. Load connections run through Service Schedule 3 (line extensions), where the study charge equals APS’s actual estimated cost to prepare the work — not a fixed tariff number. The tiered deposits you will find online ($20K / $40K feasibility & system-impact, or $5K + $100K + $200K) are GENERATION interconnection (Schedule 6 / FERC queue reform) and do NOT apply to a data-center load. Both are shown below so the distinction is unambiguous.

### A.  Large-Load Study & Connection Costs (Service Schedule 3 — applies to data centers)

| Cost item | Amount / basis | Notes | Confidence |
| --- | --- | --- | --- |
| Preliminary sketch + rough cost estimate | No charge | Provided by APS on request (§27.1) | GROUNDED |
| Special study / detailed design / cost estimate | = APS’s estimated cost to prepare it (no fixed fee) | Credited to construction cost if you proceed; NON-REFUNDABLE if you don’t (§27.1) | GROUNDED |
| Cost-sharing test | “Economic Feasibility”: projected annual delivery revenue vs. cost | Determines free allowance vs. refundable advance | GROUNDED |
| Construction cost above allowance | Paid in full by applicant | Due at Line Extension Agreement signing, before APS installs facilities | GROUNDED |
| CIAC (≥ 15 MW, transmission service) | Full cost of transmission facilities, in lieu of buying them | APS may finance at its WACC up to 10 years (XHLF option) | GROUNDED |
| Collateral & minimum bill | Set per Electric Supply Agreement — not publicly fixed | New / higher terms proposed in 2025 rate case (see §6) | UNKNOWN (per ESA) |
| Long-lead equipment | Transmission transformers, breakers — 2–4 yr lead | Drives schedule, not a fee | MARKET NORM |

Industry comparable for a load study/evaluation fee (NON-APS, order-of-magnitude only): Tri-State proposes ~$80K @ 45 MW / $150K @ 100 MW / $250K @ 200 MW.

### B.  Generation Interconnection Deposits (Schedule 6 / LGIP — REFERENCE ONLY, not load)

Listed only so these are not mistaken for load costs. These apply to generators (solar, storage, gas), not to a data-center load.

| Stage / item | Deposit | Confidence |
| --- | --- | --- |
| Feasibility Study (≥ 69 kV) | $20,000 | GROUNDED |
| System Impact Study (≥ 69 kV) | $40,000 | GROUNDED |
| Facilities Study | Per Schedule 6 (actual cost; prior study deposits credited) | GROUNDED |
| Queue-reform application package | $5,000 non-refundable app fee + ~$100,000 study deposit + $200,000 commercial-readiness deposit | GROUNDED |
| Large Generator Interconnection Agreement (LGIA) | $160,000 (≤ 75 MW) / $250,000 (≥ 76 MW) | GROUNDED |

Bottom line: for a data-center load, budget the study as APS’s actual cost to prepare it (credited toward construction if you build) — the material money is CIAC + collateral at the firm gate, which can run tens of millions for a large campus, not the study fee.

# 6.  Regulatory Risk (Active Dockets)

ACC docket E-01345A-25-0105 (2025 rate case): APS proposes >45% rate increase for extra-large users, new minimum-bill and collateral requirements, “bring your own power” cost assignment, accelerated service via long-term contracts with up-front infrastructure contributions, and formula rates. PROPOSED, not yet effective.

ACC docket E-00000A-25-0069 (data-center inquiry): Commission-wide review of data-center / large-load rate classifications and ratepayer protection. APS and SRP have proposed their own queue processes and standard agreements requiring up-front financial support. Terms not yet quantified.

Net: cost-allocation, collateral, and minimum-bill terms for Arizona large load are actively in flux through 2026. Verify against the live docket before committing.

# 7.  Deal Notes

Generation adequacy is the dominant gating risk, not wires availability — confirm APS can supply energy at the site/size/timing before valuing the wires path.

Expect to be pushed toward BYOP / demand-flexibility and a 50% carbon-free commitment to access the Econ-Dev & Sustainability features.

The 92% load-factor floor is data-center-friendly (steady load); the tariff exempts billing cycles where a miss is solely due to in-cycle load growth — watch ramp mechanics.

Real capital exposure is CIAC + collateral at the firm gate, which can run tens of millions for a large campus.

# 8.  To Upgrade This Analysis

Obtain these to move from ESTIMATED to GROUNDED:

APS large-load process guide / a real facilities-study scoping — flips the stage map, study cost, and firm-gate timing. (Highest value.)

ACC eDocket E-01345A-25-0105 filings — quantifies proposed collateral, minimum bill, BYOP terms.

ACC eDocket E-00000A-25-0069 filings — quantifies data-center-specific rules.

SRP large-load process guide + rate schedule, and TEP large-load tariff — for full Arizona coverage.

## Sources

APS Rate Schedule XHLF, A.C.C. No. 6067, Rev 3 (Decision No. 79293), effective March 8, 2024.

APS Service Schedule 3 (Extensions of Electric Distribution Lines and Services), A.C.C. No. 6217, Rev 16, effective March 8, 2024 — §27.1 study/design, Economic Feasibility, allowances.

APS Service Schedule 6 (Interconnection Study, Non-FERC Generation) and APS LGIP/queue-reform filings — source of the generation deposit figures.

APS — “Data Centers: How We’re Protecting Customers While Planning for Big Energy Needs.”

Arizona Corporation Commission — Data Center/Large Load Workshop Highlights (April 2026).

APS 2025 Rate Case (ACC docket E-01345A-25-0105).

ACC data-center inquiry (docket E-00000A-25-0069).

EUCI — Utilities adopt large load tariffs (Tri-State evaluation-fee comparable).